## History
Ver | Date | Note
0.1 |  | First draft
0.2 | 2019-06-20 | Remove unuseful field from xx_Table_Alarm this due to the fact that the HR/IR alarms are always a register Modified Dim now is in bit instead of byte this to mantain the same rapresentation between different tools

## MemoryCalculator
Max vars | Description | Size | Total
| Header Size | 59 | 59
21 | Coils_table record size low polling | 4 | 84
5 | DI_Table record size low polling | 4 | 20
19 | HR_Table record size low polling | 20 | 380
2 | IR_Table record size low polling | 20 | 40
15 | Coils_table record size | 4 | 60
4 | DI_Table record size | 4 | 16
24 | HR_Table record size | 20 | 480
2 | IR_Table record size | 20 | 40
25 | alr Coils_table record size | 4 | 100
1 | DI_Table record size | 4 | 4
1 | HR_Table record size | 5 | 5
1 | IR_Table record size | 5 | 5
120 |  | Total | 1293
Note on A1: insert the number of variables to be monitored

## Header
Description | Size bytes | Type | Value / example | Note
Header signature | 8 | String | 'GME_MBT' | a fixed signature value, 'G' is the first character returned \x0 final
Header version | 2 | INT16 | 0x0100 | little endian notation (* we assume that in this mode the reading is more simple )
Model GUID | 16 | byte array | (first) 42 83 7e f5 44 b3 41 67 a0 d6 95 63 c6 e7 30 f8(last) | a byte array, the values are store in the same order used by CAREL cloud
Model version | 4 | UINT32 | 0x01 00 00 00 | major minor fix + letter (a..z)
RS485 Stop bit | 1 | Byte |  | 1 = 1 stop 2= 2 stop bit
RS485 Parity bit | 1 | Byte |  | 0 = NONE 1 = Odd 2 = Even
Number of coils row in the table low polling | 2 | INT16 | 0x03 | little endian notation (* we assume that in this mode the reading is more simple )
Number of discrete input in the table low polling | 2 | INT16 | 0x02 | little endian notation (* we assume that in this mode the reading is more simple )
Number of holding registers in the table low polling | 2 | INT16 | 0x10 | little endian notation (* we assume that in this mode the reading is more simple )
Number of input register in the table low polling | 2 | INT16 | 0x02 | little endian notation (* we assume that in this mode the reading is more simple )
Number of coils row in the table high polling | 2 | INT16 | 0x03 | little endian notation (* we assume that in this mode the reading is more simple )
Number of discrete input in the table high polling | 2 | INT16 | 0x02 | little endian notation (* we assume that in this mode the reading is more simple )
Number of holding registers in the table high polling | 2 | INT16 | 0x10 | little endian notation (* we assume that in this mode the reading is more simple )
Number of input register in the table high polling | 2 | INT16 | 0x02 | little endian notation (* we assume that in this mode the reading is more simple )
Number of alarm coils row in the table | 2 | INT16 | 0x03 | little endian notation (* we assume that in this mode the reading is more simple )
Number of alarm discrete input in the table | 2 | INT16 | 0x02 | little endian notation (* we assume that in this mode the reading is more simple )
Number of alarm bit field holding registers in the table | 2 | INT16 | 0x10 | little endian notation (* we assume that in this mode the reading is more simple )
Number of alarm input register in the table | 2 | INT16 | 0x02 | little endian notation (* we assume that in this mode the reading is more simple )
Table CRC16 | 2 | INT16 |  | The CRC of the whole file is at the end of the file, put here for simplicity
1

## (C)oils_Table_low
Description | Size bytes | Example | Note
Alias | 2 | 33
MBaddr | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )

## (C)oils_Table
Description | Size bytes | Example | Note
Alias | 2 | 33
MBaddr | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )

## (C)oils_Table_alarm
Description | Size bytes | Example | Note
Alias | 2 | 33
MBaddr | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )

## DI_Table_low
Description | Size bytes | Example | Note
Alias | 2 | 33
MBaddr | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )

## DI_Table
Description | Size bytes | Example | Note
Alias | 2 | 33
MBaddr | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )

## DI_Table_alarm
Description | Size bytes | Example | Note
Alias | 2 | 33
MBaddr | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )

## HR_Table_low
Description | Size bytes | Example | Note
Alias | 2 | 33
Address | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )
flags | 1 | 0x01 | bit 0 = is FIXEDPOINT bit 1 = bit 2 = is IEEE bit 3 = bit 4 = bit 5 = bit 6 = is signed bit 7 = is Big Endian
Dim | 1 | 0x10 | Number of bits to be read to read 32 bit values we need to read 2 contigous registers in the same read operation this field indicate 16 > 1HR or 32 > 2 HR to be read if this value = 32 the system do a ReadMultiple registers command (0x10) with quantity of inputs = 2
bitposition | 1
len | 1 |  | dimension of the data field to rapresent a nibble len=4
lin A | 4 |  | This value is an IEEE number
lin B | 4 |  | This value is an IEEE number
Hysteresis | 4 | 0x01 | This value is an IEEE number

## HR_Table
Description | Size bytes | Example | Note
Alias | 2 | 33
Address | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )
flags | 1 | 0x01 | bit 0 = is FIXEDPOINT bit 1 = bit 2 = is IEEE bit 3 = bit 4 = bit 5 = bit 6 = is signed bit 7 = is Big Endian
Dim | 1 | 0x10 | Number of bits to be read to read 32 bit values we need to read 2 contigous registers in the same read operation this field indicate 16 > 1HR or 32 > 2 HR to be read if this value = 32 the system do a ReadMultiple registers command (0x10) with quantity of inputs = 2
bitposition | 1
len | 1 |  | dimension of the data field to rapresent a nibble len=4
lin A | 4 |  | This value is an IEEE number
lin B | 4 |  | This value is an IEEE number
Hysteresis | 4 | 0x01 | This value is an IEEE number

## HR_Table_alarm
Description | Size bytes | Example | Note
Alias | 2 | 33
Address | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )
bitposition | 1

## IR_Table_low
Description | Size bytes | Example | Note
Alias | 2 | 33
Address | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )
flags | 1 | 0x01 | bit 0 = is FIXEDPOINT bit 1 = bit 2 = is IEEE bit 3 = bit 4 = bit 5 = bit 6 = is signed bit 7 = is Big Endian
Dim | 1 | 0x10 | Number of bits to be read to read 32 bit values we need to read 2 contigous registers in the same read operation this field indicate 16 > 1HR or 32 > 2 HR to be read if this value = 32 the system do a ReadMultiple registers command (0x10) with quantity of inputs = 2
bitposition | 1
len | 1 |  | dimension of the data field to rapresent a nibble len=4
lin A | 4 |  | This value is an IEEE number
lin B | 4 |  | This value is an IEEE number
Hysteresis | 4 | 0x01 | This value is an IEEE number

## IR_Table
Description | Size bytes | Example | Note
Alias | 2 | 33
Address | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )
flags | 1 | 0x01 | bit 0 = is FIXEDPOINT bit 1 = bit 2 = is IEEE bit 3 = bit 4 = bit 5 = bit 6 = is signed bit 7 = is Big Endian
Dim | 1 | 0x10 | Number of bits to be read to read 32 bit values we need to read 2 contigous registers in the same read operation this field indicate 16 > 1HR or 32 > 2 HR to be read if this value = 32 the system do a ReadMultiple registers command (0x10) with quantity of inputs = 2
bitposition | 1
len | 1 |  | dimension of the data field to rapresent a nibble len=4
lin A | 4 |  | This value is an IEEE number
lin B | 4 |  | This value is an IEEE number
Hysteresis | 4 | 0x01 | This value is an IEEE number

## IR_Table_alarm
Description | Size bytes | Example | Note
Alias | 2 | 33
Address | 2 | 0x410 | little endian notation (* we assume that in this mode the reading is more simple )
bitposition | 1

## Binary_Example
1 | 0x47 | G
2 | 0x4d | M
3 | 0x45 | E
4 | 0x5f | _
5 | 0x4d | M
6 | 0x42 | B
7 | 0x54 | T
8 | 0x00 | /0
9 | 0x01 | Header version
10 | 0x00
11 | 0x10 | Model GUID
12 | 0x0f
13 | 0x0e
14 | 0x0d
15 | 0x0c
16 | 0x0b
17 | 0x0a
18 | 0x09
19 | 0x08
20 | 0x07
21 | 0x06
22 | 0x05
23 | 0x04
24 | 0x03
25 | 0x02
26 | 0x01
27 | 0x01
28 | 0x00 | Model Version
29 | 0x00
30 | 0x00
31 | 0x01 | Rs485 Stop Bit
32 | 0x00 | Rs485 parity
33 | 0x03
34 | 0x00 | Coil
35 | 0x02
36 | 0x00 | DI | Low Polling
37 | 0x01
38 | 0x00 | HR
39 | 0x01
40 | 0x00 | IR
41 | 0x03
42 | 0x00 | Coil
43 | 0x00
44 | 0x00 | DI | High Polling
45 | 0x01
46 | 0x00 | HR
47 | 0x05
48 | 0x00 | IR
49 | 0x05
50 | 0x00 | Coil
51 | 0x00
52 | 0x00 | DI | Allarm Polling
53 | 0x00
54 | 0x00 | HR
55 | 0x00
56 | 0x00 | IR
57 | 0x33
58 | 0x00 | Alias
59 | 0x21
60 | 0x00 | MBAddr
61 | 0x34
62 | 0x00 | Alias | Coil Low Poll
63 | 0x22
64 | 0x00 | MBAddr
65 | 0x35
66 | 0x00 | Alias
67 | 0x22
68 | 0x00 | MBAddr
69 | 0x047
70 | 0x00 | Alias
71 | 0x30
72 | 0x00 | MBAddr
73 | 0x48
74 | 0x00 | Alias | Coil high Poll
75 | 0x34
76 | 0x00 | MBAddr
77 | 0x49
78 | 0x00 | Alias
79 | 0x50
80 | 0x00 | MBAddr
81 | 0x71
82 | 0x00 | Alias
83 | 0x01
84 | 0x00 | MBAddr
85 | 0x72
86 | 0x00 | Alias
87 | 0x02
88 | 0x00 | MBAddr
89 | 0x73 |  | Coil Allarm poll
90 | 0x00 | Alias
91 | 0x03
92 | 0x00 | MBAddr
93 | 0x74
94 | 0x00 | Alias
95 | 0x04
96 | 0x00 | MBAddr
97 | 0x75
98 | 0x00 | Alias
99 | 0x05
100 | 0x00 | MBAddr
101 | 0x36
102 | 0x00 | Alias
103 | 0x23
104 | 0x00 | MBAddr | DI low poll
105 | 0x37
106 | 0x00 | Alias
107 | 0x24
108 | 0x00 | MBAddr
109 | 0x38
110 | 0x00 | Alias
111 | 0x25
112 | 0x00 | MBAddr
113 | 0x01 | fixed
114 | 0x01 | dim
115 | 0x00 | bit
116 | 0x00 | len
117 | 0x00 |  | HR Low Poll
118 | 0x00 | lin A
119 | 0x00
120 | 0x00
121 | 0x00
122 | 0x00 | lin B
123 | 0x00
124 | 0x00
125 | 0x01
126 | 0x00 | Hysteresis
127 | 0x00
128 | 0x00
129 | 0x53
130 | 0x00 | Alias
131 | 0x03
132 | 0x00 | MBAddr
133 | 0x01 | fixed
134 | 0x01 | dim
135 | 0x00 | bit
136 | 0x00 | len
137 | 0x00 |  | HR high Poll
138 | 0x00 | lin A
139 | 0x00
140 | 0x00
141 | 0x00
142 | 0x00 | lin B
143 | 0x00
144 | 0x00
145 | 0x01
146 | 0x00 | Hysteresis
147 | 0x00
148 | 0x00
149 | 0x39
150 | 0x00 | Alias
151 | 0x26
152 | 0x00 | MBAddr
153 | 0x01 | fixed
154 | 0x01 | dim
155 | 0x00 | bit
156 | 0x00 | len
157 | 0x00 |  | IR Low Poll
158 | 0x00 | lin A
159 | 0x00
160 | 0x00
161 | 0x00
162 | 0x00 | lin B
163 | 0x00
164 | 0x00
165 | 0x01
166 | 0x00 | Hysteresis
167 | 0x00
168 | 0x00
169 | 0x55
170 | 0x00 | Alias
171 | 0x01
172 | 0x00 | MBAddr
173 | 0x01 | fixed
174 | 0x01 | dim
175 | 0x00 | bit
176 | 0x00 | len
177 | 0x00 |  | IR high Poll
178 | 0x00 | lin A
179 | 0x00
180 | 0x00
181 | 0x00
182 | 0x00 | lin B
183 | 0x00
184 | 0x00
185 | 0x01
186 | 0x00 | Hysteresis
187 | 0x00
188 | 0x00
189 | 0x56
190 | 0x00 | Alias
191 | 0x02
192 | 0x00 | MBAddr
193 | 0x01 | fixed
194 | 0x01 | dim
195 | 0x00 | bit
196 | 0x00 | len
197 | 0x00 |  | IR high Poll
198 | 0x00 | lin A
199 | 0x00
200 | 0x00
201 | 0x00
202 | 0x00 | lin B
203 | 0x00
204 | 0x00
205 | 0x01
206 | 0x00 | Hysteresis
207 | 0x00
208 | 0x00
209 | 0x57
210 | 0x00 | Alias
211 | 0x03
212 | 0x00 | MBAddr
213 | 0x01 | fixed
214 | 0x01 | dim
215 | 0x00 | bit
216 | 0x00 | len
217 | 0x00 |  | IR high Poll
218 | 0x00 | lin A
219 | 0x00
220 | 0x00
221 | 0x00
222 | 0x00 | lin B
223 | 0x00
224 | 0x00
225 | 0x01
226 | 0x00 | Hysteresis
227 | 0x00
228 | 0x00
229 | 0x58
230 | 0x00 | Alias
231 | 0x04
232 | 0x00 | MBAddr
233 | 0x01 | fixed
234 | 0x01 | dim
235 | 0x00 | bit
236 | 0x00 | len
237 | 0x00 |  | IR high Poll
238 | 0x00 | lin A
239 | 0x00
240 | 0x00
241 | 0x00
242 | 0x00 | lin B
243 | 0x00
244 | 0x00
245 | 0x01
246 | 0x00 | Hysteresis
247 | 0x00
248 | 0x00
249 | 0x59
250 | 0x00 | Alias
251 | 0x05
252 | 0x00 | MBAddr
253 | 0x01 | fixed
254 | 0x01 | dim
255 | 0x00 | bit
256 | 0x00 | len
257 | 0x00 |  | IR high Poll
258 | 0x00 | lin A
259 | 0x00
260 | 0x00
261 | 0x00
262 | 0x00 | lin B
263 | 0x00
264 | 0x00
265 | 0x01
266 | 0x00 | Hysteresis
267 | 0x00
268 | 0x00
269 | 0x7c | CRC16
270 | 0xf7