## commands
| req | [8 empty] | mqtt
| cmd | requires response | response type | response content | [5 empty] | qos | retain | polling engine status | flush before execute | reboot after | note
hello |  | no | [10 empty] | NA
status |  | no | [10 empty] | NA
mobile |  | no | [10 empty] | NA
alarms |  | no | [10 empty] | NA
values |  | no | [10 empty] | NA
set_gw_config | 1 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | no | no | (A)
reboot | 2 | yes | header | [8 empty] | stop | yes | yes | (A)
scan_line | 3 | yes | header+other | ver | rto | cmd | res | dev | ans |  |  | stop | no | no | (A)
set_lines_config | 4 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | no | no | (A)
set_devs_config | 5 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | yes | yes | (A)
read_values | 6 | yes | header+other | ver | rto | cmd | res | ali | val |  |  | stop | no | no | (A)
write_values | 7 | yes | header+other | ver | rto | cmd | res | ali | val |  |  | stop | no | no | (A)
update_gw_firmware | 10 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | yes | yes | (A)
update_dev_firmware | 11 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | yes | no | (A)
flush_values | 12 | yes | header | ver | rto | cmd | res | [5 empty] | NA | no
update_ca_certificate | 13 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | yes | no | (A)
send_mb_adu | 14 | yes | header+other | ver | rto | cmd | res | seq | adr |  |  | stop | yes | no | (A)
send_mb_pass_through | 15 | yes | header+other | ver | rto | cmd | res | pas | [5 empty] | no
change_credentials | 16 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | yes | yes | (A)
start_engine | 17 | yes | header | ver | rto | cmd | res |  |  |  |  | stop | no | no
stop_engine | 18 | yes | header | ver | rto | cmd | res |  |  |  |  | running | yes | no
(A) if the engine is running the system enter automatically in stop engine mode

## from GME
payload | meaning | TAG | data type (max occupation) | possible values | notes
hello | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| part number | pn | C_CHAR[16]
| hw version | hwv | C_UINT16
| fw version | fwv | C_UINT16
| unix epoch of machine first boot | btm | C_TIME
| baud rate | bau | C_UINT32 | 4800,9600,19200,38400,115200
| mqtt version | mqv | C_UINT16[3] | 0/0/0: NA | 3/1/1=3.1.1
| device | dev | C_UINT16
| guid | gid | C_BYTE[16]
| CRC of model file | crc | C_UINT16
| request identifier | cid | C_UINT16
status | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| current time | t | C_TIME
| seconds since power on | upt | C_TIME
| free memory [bytes] | fme | C_UINT32
| polling engine status | est | C_BYTE | 0: not valid, 1: polling engine running, 2: polling engine stopped
| received signal power [dBm] | sgn | C_INT16
mobile | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| seconds since connected | gup | C_INT32
| received signal power [dBm] | sig | C_INT16 | same as sgn in status? for 2G GME yes
| current time | t | C_TIME
| imei | ime | C_BYTE[IMEI_SIZE] |  | IMEI_SIZE = 15 digits = 15 bytes
| imsi | ims | C_BYTE[IMSI_SIZE] |  | IMSI_SIZE = 15 digits = 15 bytes | (USR_TBC)
| mobile country code | mcc | C_BYTE[3] |  |  | (USR_TBC)
| mobile network code | mnc | C_BYTE[3] |  |  | (USR_TBC)
| location area code | lac | C_BYTE[16] |  |  | (USR_TBC)
| cell id | cel | C_BYTE[16] |  |  | (USR_TBC)
| cell id for umts | uci | C_BYTE[16] |  |  | (USR_TBC)
alarms | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| type of alarm | aty | C_BYTE | 0: not valid, 1: variable, 2:device
| alarm alias | ali | C_CHAR[ALIAS_SIZE] | "" if type not variable | ALIAS_SIZE "1..65535" = 7 bytes
| alarm code | aco | C_BYTE | if type is device: 0: not valid, >=1 device alarm; if type is variable: 0
| device id | did | C_UINT16
| unix epoch in which alarm started | st | C_TIME | always set
| unix epoch in which alarm ended | et | C_TIME | 0: alarm message is start alarm, !=0: alarm message is stop alarms
values | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| counter | cnt | C_UINT32 | increases monotonically every time a values is sent
| unix epoch of machine first boot | btm | C_TIME
| current epoch | t | C_TIME
| device id | did | C_UINT16
| map of sampled values | vls |  | follows a list of entries, size of list depends on GME memory limitations
|  | "alias":"value" | C_CHAR[ALIAS_SIZE]:C_CHAR[VAL_SIZE] |  | ALIAS_SIZE "1..65535" = 7 bytes VAL_SIZE = +/- 1.18e+/-38 =10 bytes
| frame counter | frm | C_INT16 | frm starts at 1, increases by 1 at each frame at same t last frame has frm -n, where n is total number of frames
set_gw_config set_lines_config update_gw_firmware update_dev_firmware update_ca_certificate change_credentials | set_gw_config set_lines_config update_gw_firmware update_dev_firmware update_ca_certificate change_credentials | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
|  | respond to | rto | C_CHAR[RTO_SIZE] | as in request | RTO_SIZE=48
|  | command code | cmd | C_UINT16
|  | command execution result | res | C_INT16 | 0: ok, -1: invalid, >=1: error
set_devs_config | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] | as in request | RTO_SIZE=48
| command code | cmd | C_UINT16
| slave address | dev | C_UINT16
| command execution result | res | C_INT16 | 0: ok, -1: invalid, >=1: error
scan_line | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] | as in request
| command code | cmd | C_UINT16
| slave address | dev | C_UINT16
| response to Modbus command 17 | ans | C_BYTE[RET_SIZE] |  | RET_SIZE=512 bytes ? Bilato si perchè è il massimo payload ad oggi conosciuto di una risposta cmd17
read_values | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] | as in request
| command code | cmd | C_UINT16
| command execution result | res | C_INT16 | 0: ok, -1: invalid, >=1: error
| address of connected device | dev | C_UINT16
| current time | t | C_TIME
| slave address | dev | C_UINT16
| alias | ali | C_CHAR[ALIAS_SIZE]
| value | val | C_CHAR[VAL_SIZE]
write_values | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] | as in request
| command code | cmd | C_UINT16
| command execution result | res | C_INT16 | 0: ok, -1: invalid, >=1: error
| current time | t | C_TIME
| slave address | dev | C_UINT16
| alias | ali | C_CHAR[ALIAS_SIZE]
| value | val |  | null
send_mb_adu | payload version | ver | C_UINT16 | 256 | 256 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] | as in request
| command code | cmd | C_UINT16
| adu identifier | seq | C_UINT16 | same as in request
| Modbus response | adr | C_BYTE[MBADU_SIZE] | val renamed to adr (val already used) | MBADU_SIZE=512? adr rinominato (era val) Bilato un comando adu può tornare di tutto ma fissiamo a 512 bytes massimo così recuperiamo il buffer del cmd17.
send_mb_pass_through | payload version | ver | C_UINT16 | 256
| respond to | rto | C_CHAR[RTO_SIZE]
| code command | cmd | C_UINT16 | 18
| required operation | pas | C_UINT16 | 0:invalid, 1:pass through enabled, 2:pass through disabled, 3:get status | pas perché val già usato

## from cloud
payload | meaning | TAG | data type (max occupation) | possible values | notes
change_credentials | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 15
| username | usr | C_CHAR[USR_SIZE] |  | USR_SIZE
| password | pwd | C_CHAR[PWD_SIZE] |  | PWD_SIZE
set_gw_config | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE]
| code command | cmd | C_UINT16 | 1
| values published every pva seconds | pva | C_UINT16
| status published every pst seconds | pst | C_UINT16
| mqtt keep alive interval | mka | C_UINT16
| low speed sampling | lss | C_UINT16
| high speed sampling | hss | C_UINT16
scan_line | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 3
set_lines_config | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE]
| code command | cmd | C_UINT16 | 4
| baud rate | bau | C_UINT32 | 4800/9600/19200/38400/56800/115200
| connector | con | C_BYTE | 0: not valid, 1: RS485, 2: TTL
set_devs_config | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 5
| device address | dev | C_UINT16
| username | usr | C_CHAR[USR_SIZE] |  | 34 char
| password | pwd | C_CHAR[PWD_SIZE] |  | 34 char
| uri | uri | C_CHAR[URI_SIZE] |  | URI_SIZE Bilato si era detto max 64 char per tutti gli URI
| device id | did | C_UINT16
| transaction id | cid | C_UINT16
read_values | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 6
| alias | ali | C_CHAR[ALI_SIZE]
| Modbus function | fun | C_BYTE
| Modbus address | adr | C_BYTE
| bits | dim | C_BYTE
| position | pos | C_BYTE
| length | len | C_BYTE
| val*a+b | a | C_CHAR[VAL_SIZE]
| val*a+b | b | C_CHAR[VAL_SIZE]
| flags | flg | C_BYTE | 0=is FIXEDPOINT bit 1 = NA bit 2 = is IEEE bit 3 = NA bit 4 = NA bit 5 = NA bit 6 = is signed bit 7 = is Big Endian
write_values | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 7
| alias | ali | C_CHAR[ALI_SIZE] |  | ALIAS_SIZE "1..65535" = 7 bytes
| value | val | C_CHAR[VAL_SIZE] |  | VAL_SIZE = +/- 1.18e+/-38 =10 bytes
| Modbus function | fun | C_BYTE
| Modbus address | adr | C_BYTE
| bits | dim | C_BYTE
| position | pos | C_BYTE
| length | len | C_BYTE
| val*a+b | a | C_CHAR[VAL_SIZE]
| val*a+b | b | C_CHAR[VAL_SIZE]
| flags | flg | C_BYTE | 0=is FIXEDPOINT bit 1 = NA bit 2 = is IEEE bit 3 = NA bit 4 = NA bit 5 = NA bit 6 = is signed bit 7 = is Big Endian
update_gw_firmware | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 10
| username | usr | C_CHAR[USR_SIZE]
| password | pwd | C_CHAR[PWD_SIZE]
| uri | uri | C_CHAR[URI_SIZE]
| staring Modbus file index | fid | C_UINT16
| transaction id | cid | C_UINT16
update_dev_firmware | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 11
| username | usr | C_CHAR[USR_SIZE]
| password | pwd | C_CHAR[PWD_SIZE]
| uri | uri | C_CHAR[URI_SIZE]
| starting Modbus file index | fid | C_UINT16
| number of seconds needed to perform a reboot after an upgrade | wet | C_UINT16
update_ca_certificate | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 13
| crc of certificate | crc | C_UINT16
| username | usr | C_CHAR[USR_SIZE]
| password | pwd | C_CHAR[PWD_SIZE]
| uri | uri | C_CHAR[URI_SIZE]
send_mb_adu | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 14
| adu identifier | seq | C_UINT16
| Modbus request | adu | C_BYTE[ADU_SIZE]
reboot | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 2
| transaction id | cid | C_UINT16
start_engine | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 16
stop_engine | payload version | ver | C_UINT16 | 256 | 257 == 0x100 > V.1.00
| respond to | rto | C_CHAR[RTO_SIZE] |  | 48 char
| code command | cmd | C_UINT16 | 17
send_mb_pass_through | payload version | ver | C_UINT16 | 256
| respond to | rto | C_CHAR[RTO_SIZE]
| code command | cmd | C_UINT16 | 18
| required operation | pas | C_UINT16 | 0:invalid, 1:pass through enabled, 2:pass through disabled, 3:get status | pas perché val già usato