## V.0.01
Test ID | Summary | Preconditions | Expected Result | Result | Notes
#REF! | Verify if the linearization is applied
#REF! | Verify if the hysteresis is applied
33
Si usa il cpCO ono 2 file di modello con diffreneti valori di linearizzazione a parità di parametro
Si usa il cpCO ono 2 file di modello con diffreneti isteresi a parità di parametro
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## rtc configuration
Test ID | Summary | Preconditions | Expected Result | Result | Notes
1 | RTC initialization with NTP reachable | 1. the device is powered off 2. a test AP configured 3. the default NTP server must be reachable, check it with a PC. 4. power on the device | Check with the debug console that the INT32 var that contain the UTC value, the number must be comparable with the current time returned by https://www.epochconverter.com/
2 | RTC initialization with NTP unreachable | 1. a test AP configured as previous test 2. set through the configuration page a bad NTP URI ie. "bad.ntp.org". 3. power on the device | Check with the debug console that the INT32 var that contain the UTC value, the converted value is within 1970/01/01 range use https://www.epochconverter.com/ GME must not reboot, it must be possible to reconfigure the ntp server using the web page
3 | Test the power on time value | The system is running and correctly synchronized with the NTP server | Inspect the variable Power_On_Time in hello packet and this report the UTC time of start up
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## wifi configuration
Test ID | Summary | Preconditions | Expected Result | Result | Notes
1 | Test that device AP emit the right SSID | 1. A Windows PC with a WiFi adapter. Repeat all the below tests using a a smartphone. 2. device with AP mode in default condition | Use the PC/Smartphone to discover the SSID, you will find an SSID like "cgatem_ xxyyzz" where xxyyzz are tha last MAC address numbers of the device
2 | Test that device AP is connectable | 1. A Windows PC with a WiFi adapter (smartphone) 2. device with AP mode in default condition 3. Use the PC and connect to the SSID "cgatem_ xxyyzz" | 1. the PC is able to connect to the AP 2. the AP doesn't ask for a password 3. the DHCP of the device assign the address 10.10.100.10 to the PC 4. the default gateway returned is 10.10.100.254 Note. Use command line console with the "ipconfig /all" command to verify the above data.
3 | Test that the device webserver respond | 1. A Windows PC with a WiFi connected to the AP | 1. open a browser and type "http://10.10.100.10" 2. the browser shows the device change credentials page
4 | Test the device webserver change credentials page | 1. A Windows PC with a WiFi connected to the AP 2. test 3 completed | 1. the browser shows the device change cred page 2. insert new credentials and submit 3. the login page is shown (go to next test)
5 | Test the device webserver login page | 1. A Windows PC with a WiFi connected to the AP | 1. the login page is able to receive the login information 2. When submit is clicked, the config page appears
6 | Test the device webserver configuration page | 1. A Windows PC with a WiFi connected to the AP 2. browser pointing to "http://10.10.100.10". set the parameters as follow - AP SSID "your_ap" - AP Security : WPA - AP Password : "your_pwd" - DHCP on | 1. the page is properly shown 2. it is possible to see the list of reachable aps, selecting scan. 3. If dhcp is disabled static textboxes can be edited 4. show password boxes hide/show passwords 5. if ssid, password, ip in ap options are left blank the page is not submitted (password must be 8 characters)
7 | Test that the device is able to connect to an AP manually selected | 1. a test AP connected to the internet configured as follow : - SSID "TEST_AP" - Security : WPA - Password : "12345678" - DHCP on 2. a device with all the connections parameter already configured as above | 1. the device is able to connect to the AP 2. through the debug console of the device, check that a. the IP address is 10.10.100.10 b. the default gateway is 10.10.100.254 c. the DNS is 8.8.8.8/8.8.4.4
8 | Test that the device is able to connect to an AP selected with a wifi scan | 1. a test AP connected to the internet configured as follow : - SSID "TEST_AP" - Security : WPA - Password : "12345678" - DHCP on 2. a device with all the connections parameter already configured as above 3. select the WPS choice and then press the WPS button on the AP (according to your AP manual) | 1. Check that hello message contains: a. part number (GTW000M2G0 for wifi model) b. hw version and fw version c. boot time (btm) which must be reasonable d. baud rate (which must coincide with that previously set) e. mqtt version, 3.1.1 f. Modbus addres of connected device (dev) g. model guid, retrieved from model file h. crc of model file i. cid, as described in tests above
9 | Test that the device is able to connect to an AP configured with WPS | 1. check that every t_pst (configured with set_gw_config) a status message is sent | 1. Check that status message contains: a. epoch time of the moment message is sent b. upt, seconds since power on c. free memory (fme, in bytes) d. status of polling engine (est, 1 running, 2 stopped, 0 not valid) e. received signal strenght (sgn) (meaningful values around -60...-30 dBm
9 | Test that the device is able to connect to an AP with static IP configuration | 1. a test AP connected to the internet configured as follow : - SSID "TEST_AP" - Security : WPA - Password : "12345678" 2. a device with all the connections parameter already configured as above 3. select DHCP off 4. fill the textboxes with IP address and other static configuration info | 1. the device is able to connect to the AP 2. through the debug console of the device, check that the IP address, the default gateway and the DNS are the ones configured
10 | Test if the device configuration is maintained between power on/off cycle. | 1. if the previous tests are ok, power off the device and wait 5 seconds. 2. power on again the device | 1. the device is able to connect to the AP 2. through the debug console of the device, check that a. the IP address is 10.10.100.10 gateway is 10.10.100.254 c. the DNS is 8.8.8.8/8.8.4.4 3. open a browser and type "http://10.10.100.10" the device configuration page contains the values set in the previous test.
11 | Test ntp server setting recovery | 1. in config page set a non existing ntp server, as bad.ntp.org) | 1. after reboot, check from debug console messages that time was not recovered 2. check that it is still possible to access the configuration page to reset the right server (pool.ntp.org) 3. verify that after a new reboot, time is properly obatined
12 | Test change in ap options | 1. in config page, change ap ssid name and password | 1. after reboot, check that the GME is showing with new ap name and password
13 | Test ap options hide ssid | 1. in config page, fill in mandatory textboxes then click Hide ssid | 1. after reboot, GME ssid is not visible with a scan from a PC or a phone, it can be manually set and connection must work
14 | payload-stop_engine.cbor | 1. Check that stop engine request actually stops polling | 1. Check that GME sends a response 2. Check that polling is stopped (no more values sent, even if some are forcedly changing) 3. Wait for a status message and check that est field is 2
15 | payload-start_engine.cbor | 1. Check that start engine request actually starts polling | 1. Check that GME sends a response 2. Check that polling is started (values are sent, at sampling times if they are changing) 3. Wait for a status message and check that est field is 1
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## mqtt communication
Test ID | Summary | Preconditions | Expected Result | Result | Notes
0 |  | All below tests require that GME is connected to an AP and that a MQTT server is reachable. It also requires that a c.pCO is properly connected to the serial port of the GME, that configuration is completed and GME has a valid model on board. Use a proper application for c.pCO showing some alarm variables, and a reasonable number of HR, IR, DI and COIL. Use MQTTClientSimulatorBinary in http://svncarel.carel.com/svn/c780_carel_cloud_engine_binary/Utility/MqttClientSimulatorBinary/MqttClientSimulatorBinary This works as a sniffer and shows the decoded CBOR stream
1 | payload-alarms.cbor | 1. the cpCO connected to the gateway 2. (A)select in the cpCO display the Alarm screen > select Coil_alr > change the value from 0 > 1 3. wait the first MQTT response 4. (B)select in the cpCO display the Alarm screen > select Coil_alr > change the value from 1 > 0 | Check that when the alarm is triggered a message is logged with st field containing the timestamp related to the beginning of the alarm, et 0. When the alarm reenters another alarm message is sent with st as the first message and et current time. Check all other fileds according to specification.
2 | payload-set_lines_config.cbor | 1. the mqtt simulator sends a set_lines_config request to GME. | 1. GME gets new baud rate and new connector type and stores them in nvm 2. GME internally sets a flag in nvm to state that set_lines_config was done (it can be seen from debug console) 3. GME sends a response (only header)
3 | payload-set_gw_config.cbor | 1. the mqtt simulator sends a set_gw_config request to GME. | 1. GME gets all data in request and saves it in nvm 2. GME internally sets a flag in nvm to state that set_gw_config was done (it can be seen from debug console) 3. GME sends a response (only header)
4 | payload-set_devs_config.cbor | 1. the mqtt simulator sends a set_devs_config request to GME. | 1. GME reads all data in request 2. GME downloads the model from the url indicated in the model with provided credentials 3. GME internally sets a flag in nvm to state that set_devs_config was done (it can be seen from debug console) 4. GME sends a response (only header) 5. GME reboots 6. after reboot check that hello packet contains cid as in set_devs_config request, polling starts, values packets must contain did as in set_devs_config 7. after a further reboot, cid field in hello packet must be 0
5 | payload-set_devs_config.cbor with empty url | 1. the mqtt simulator sends a set_devs_config request to GME, with url field empty. | 1. GME clears internal flag to signal that device is not configured 2. GME sends a response 3. if set_lines and set_gw already received (which is the case), GME reboots 4. Polling does not start, hello contains cid field as in last request 5. after a further reboot, hello cointains cid field 0
6 | payload_connected.cbor | 1. as soon as GME starts and connects to mqtt server, it publishes connected payload | 1. Check that sent message contains: a. ts field, epoch time of connection to mqtt server (and check that this time is reasonable), b. sta field, 1 when GME connects to server, 0 as lwt (specificare meglio)
7 | payload-hello.cbor | 1. after connect message, an hello is sent | 1. Check that hello message contains: a. part number (GTW000M2G0 for wifi model) b. hw version and fw version c. boot time (btm) which must be reasonable d. baud rate (which must coincide with that previously set) e. mqtt version, 3.1.1 f. Modbus addres of connected device (dev) g. model guid, retrieved from model file h. crc of model file i. cid, as described in tests above
8 | payload-status.cbor | 1. check that every t_pst (configured with set_gw_config) a status message is sent | 1. Check that status message contains: a. epoch time of the moment message is sent b. upt, seconds since power on c. free memory (fme, in bytes) d. status of polling engine (est, 1 running, 2 stopped, 0 not valid) e. received signal strenght (sgn) (meaningful values around -60...-30 dBm
9 | payload-scan_line.cbor | 1. the mqtt simulator sends a scan_line request to GME in different situations | 1. a c.pco with modbus address 1 is connected to GME 2. GME answers with a big message, which is the answer of the command 17 of c.pCO 3. a c.pCO with modbus address 5 is connected to GME 4. GME answers with a big message, which is the answer of the command 17 of c.pCO 5. No c.pCO connected 6. GME answers (after a long while) with (non mi ricordo cosa deve uscire)
10 | payload-change_credentials.cbor | 1. the mqtt simulator sends a change_credentials request to GME | 1. Verify that credentials are actually changed by looking at the debug console
11 | payload-update_ca.cbor | 1. the mqtt simulator sends an update_ca request to GME | 1. GME attempts to download new cert from https server. It saves new cert to other memory location (not the one currently used). See debug console for confirm. 2. GME answers with a response (only header)
12 | payload-update_dev_fw.cbor | 1. the mqtt simulator sends an update_dev_fw request to GME | 1. check with the oscilloscope that the serial communication is stopped 2. wait for response from GME saying if update was successful 3. whitin that period the cpCO will restart itself with the new application
13 | payload-update_gw_fw.cbor | 1. the mqtt simulator sends an update_gw_fw request to GME | 1. check with the oscilloscope that the serial communication is stopped 2. wait for response from GME saying if update was successful 3. the gateway will restart itself with the new FW, the confirmation is when you receive the hello packet, verify the payload content: the "fwVersion" is updated to the new version
14 | payload-stop_engine.cbor | 1. Check that stop engine request actually stops polling | 1. Check that GME sends a response 2. Check that polling is stopped (no more values sent, even if some are forcedly changing) 3. Wait for a status message and check that est field is 2
15 | payload-start_engine.cbor | 1. Check that start engine request actually starts polling | 1. Check that GME sends a response 2. Check that polling is started (values are sent, at sampling times if they are changing) 3. Wait for a status message and check that est field is 1
16 | payload-read_values.cbor | 1. Check that read_value message actually read Modbus values | 1. Attemp to read a value that is part of model 2. Check that GME answers with read value (compare it with that shown in pGD display) 3. Repeat test for each type of variable (coil, DI, IR, HR) 4. attempt to read a value that is not part of model 5. Verify steps 2 to 4
17 | payload-write_values.cbor | 1. Check that read_value message actually read Modbus values | 1. Attemp to write a value that is part of model 2. Check that GME answers as specified in RS 3. Repeat test for each type of variable (coil, DI, IR, HR) 4. attempt to read a value that is not part of model 5. Verify steps 2 to 4
18 | payload_values | 1. Check that values message is properly sent | 1. Check that values message is sent with high polling values at high sampling time 2. Check that values message is sent with low polling values at low sampling time 3. Check that no value message is sent if no change happened 4. Check that if no change happens during a T_pva (configured in set_gw_config), an empty message is sent)
19 | mqtt offline | 1. Cause an mqtt offline forcing down wifi network to which GME is connected | TODO
20 | payload-send_mb_adu-req | TODO
21 | payload_mobile | TODO
22 | fragmentation
23
24
25
26
27
28
29
30
31
32
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## modbus communication
Test ID | Summary | Preconditions | Expected Result | Result | Notes
1 | connettore RS485 | Set connector type RS485 with set_lines_config | Check that something is coming out from RS485 serial using an oscilloscope (for this to happen GME must have been previously configured, the same applies for successive tests)
2 | baud rate | a. Set baud rate to 9600 bps with a properly formed CBOR payload set_lines_config b. Set baud rate to 19200 bps with proper payload | In both cases, baud rate of the serial must change to the chosen values. Check with an oscilloscope or connecting a device having the required serial speed
3 | parity | a. Set parity to even b. Set parity to odd c. Set parity to none | Check with an oscilloscope
4 | stop bit | a. Set stop bit to 1 b. Set stop bit to 2 | Check with an oscilloscope
5 | connettore ttl | Set connector type ttl with set_lines_config | Check that something is coming out from ttl serial using an oscilloscope
6 | repeat configuration tests for ttl connector (from #2 to #4)
7 | polling delay 0 / 200 | a. Set polling delay to 0 b. Set polling delay to 200ms | Check with an oscilloscope. Verify that with polling delay 0 gme polls without delays between a packet and the following Verify that with polling delay 200 gme polls with 200ms delay between a packet and the following
| linearization | Use an application with 2 parameters having different linearization values. Change the 2 values | Verify that linearization is properly applied to both variables
| hysteresis | Use an application with 2 parameters having different hysteresis values. Change the 2 values
8 | Modbus offline
9 | model check (comprendendo anche il caso: "cosa succede se il modello è sbagliato per qualche ragione?")
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## CBOR encoding
Test ID | Summary | Preconditions | Expected Result | Result | Notes
1 | Check robustness with respect to malformed headers | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor file whose header is badly formed | When GME receives the message, it detects the badly formed header, discards it and goes back to reception |  | Tests from 1 to 14 aim at finding possible sw hunging when receiving badly formatted payloads. If a payload is syntactically correct but fields have data type different from expected, GME may have unpredictable behavior.
2 | Check robustness with respect to malformed req_set_gw_config paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_set_gw_config file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
3 | Check robustness with respect to malformed req_set_line_config paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_set_line_config file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
4 | Check robustness with respect to malformed req_set_devs_config paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_set_devs_config file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
5 | Check robustness with respect to malformed req_scan_devices paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_scan_devices file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
6 | Check robustness with respect to malformed req_read_values paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_read_values file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
7 | Check robustness with respect to malformed req_write_values paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_write_values file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
8 | Check robustness with respect to malformed req_change_cred paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_change_cred file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
9 | Check robustness with respect to malformed req_gw_update paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_gw_update file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
10 | Check robustness with respect to malformed req_dev_update paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_dev_update file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
11 | Check robustness with respect to malformed req_reboot paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_reboot file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
12 | Check robustness with respect to malformed req_start_engine paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_start_engine file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
13 | Check robustness with respect to malformed req_stop_engine paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_stop_engine file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
14 | Check robustness with respect to malformed req_update_ca paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_update_ca file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception
15 | Check connected payload | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a connected payload, it must contain all required fields, e.g. Connected: {“ver”:”100”, “ts”: 1574113297, “status”: 1} Check ts is correct time.
16 | Check hello payload | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a hello payload, it must contain all required fields. Check fields content according to RS.
17 | Check status payload (only wifi) | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a status payload, it must contain all required fields. Check fields content according to RS. Check it is sent every pst seconds.
18 | Check mobile payload (only gsm) | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a mobile payload, it must contain all required fields. Check fields content according to RS. Check it is sent every 5 minutes.
19 | Check alarms payload | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A c.pCO family controller connected | Force an alarm, check alarm payload is received and check fields content according to RS. Remove the alarm, check again alarm payload is received with proper fields in it.
20 | Check values payload | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A c.pCO family controller connected | Check values payload is received and check fields content according to RS. |  | This test does not aim at tyesting everything about values payload but just that syntax is correct.
21
22
23
24
25
26
27
28
29
30
31
32
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## default config
Test ID | Summary | Preconditions | Expected Result | Result | Notes
1 | Check default configuration is triggered by pressing button with specific procedure | 1. GME regularly running | NECESSARIO CAPIRE SE PUO' ESSERE FATTO PARTIRE IN OGNI MOMENTO O SOLO AL BOOT, DA VALUTARE INSIEME AL SECURE BOOT
2 | Check that after default configuration is triggered, GME actually starts with default configuration | 1. GME regularly running
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## gsm configuration
Test ID | Summary | Preconditions | Expected Result | Result | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## Instruction_Legenda
Legenda | Note
Device AP | The access point that the device expose
AP | The access point to which it connects
Instructions | Note
Result | PASS/FAIL they explain themselves BLOCKING means that the test is failed and block the execution of the other test.

## Support
Test result
PASS
FAIL
BLOCKING