## Revision_His.
Ver. | Descr.
0.0.1 | Initial version
Note on F1: if something was wrong a brief explanation of what happened

## Instruction_Legenda
Legenda | Note
Device AP | The access point that the device expose
AP | The access point to which it connects
Instructions | Note
Result | PASS/FAIL they explain themselves BLOCKING means that the test is failed and block the execution of the other test.

## HW_TEST
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | WiFi model check that both the power plugs work properly | 1. a suitable power supply must be availble 2. check carefully the connector polarity | The GME will be powered in both case | PASS |  | A.Chiebao | 20200804
2 | WiFi model power consuption @5V @12V @ 24V | 1. GME configured and connected to the cloud | The power consumption is below 4,2W | PASS |  | A.Chiebao | 20200804
3 | 2G model check that both the power plugs work properly | 1. a suitable power supply must be availble 2. check carefully the connector polarity | The GME will be powered in both case | PASS |  | A.Chiebao | 20200804
4 | 2G model power consuption @5V @12V @ 24V | 1. GME configured and connected to the cloud | The power consumption is below 4,2W | PASS |  | A.Chiebao | 20200804
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## Miscellaneous
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | Led status Wifi - case 1 Not configured / Not Connected to Internet | 1. an out of the box GME 2. apply the power supply | 1. the GME start and alternating flash the green/red led after that the led is off | PASS |  | A.Chiebao | 20200804
2 | Led status Wifi - case 2 Not configured / Connected to Internet | 1. configure the GME to access the Internet through a suitable AP 2. make sure that the MAC of the GME is already registered in the cloud | 1. the led green flashing | PASS |  | A.Chiebao | 20200804
3 | Led status Wifi - case 3 Configured / Connected to Internet | 1. configure the GME to access the Internet through a suitable AP 2. make sure that the MAC of the GME is already registered in the cloud 3. make sure that the GME is correctly configured | 1. the led green is ON | PASS |  | A.Chiebao | 20200804
4 | Led status Wifi - case 4 Configured / NOT Connected to Internet | 1. make sure that the MAC of the GME is already registered in the cloud 2. make sure that the GME is correctly configured | 1. the led red is OFF | PASS |  | A.Bilato | 20200910
5 | WatchDog test | 0. the test program MqttClientSimulatorBinary.exe is running and with the MAC/IMEI number set to point to the device under test 1. configure the GME to access the Internet through a suitable AP 2. make sure that the MAC of the GME is already registered in the cloud 3. when you see the "hello" message wait 2min 4. On MqttClientSimulatorBinary press button "trig WD" | 1. in a short time you will see the GME that reboot itself | NOT APPLICABLE | not implemented due to the fact that modify the FW tested this way in an modified FW | A.Bilato | 20200910
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## Security_Related
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | Only signed FW is accepted | 1. GME configured and running 2. try to upload via OTA an unsigned FW | 1. The GME restart with original FW | PASS |  | A.Chiebao | 20200804
2 | Update certificate via cable | 1. GME configured and running 2. use the update SPIFFS batch to upload a new image with new certificate | 1. verifiy that the system continua to work right 2. verify that the 3 time update counter doesn't increment | PASS | The system works but take in mind that you require 2 CA one working e one new and to check it you need the support of IoT to test it. Not easy. | A.Bilato | 2020910
3 | Updated FW via cable | WARNING! WARNING! WARNING! This test must be done only 3 times on a device, after that the only possibility to upload is through OTA. So perform it as one of the last test. 1. GME configured and running 2. connect a USB/TTL 5V adapter to the TTL port 3. press the button and power on 4. use the upgrade batch file to install a new FW 5. power off and on again | 1. verify that the new FW is installed and running properly | PASS | if the GME have an encrypted flash we must use the bash file (re-flash-encrypted.sh) in this way we flash the three usefull part (bootloader/application/partition table) | A.Chiebao | 20200804
4 | Verify that the encryption mechanism is running properly (TBC dipende dal tipo di chiave usiamo ) | 1. GME configured and running 2. power off the GME 3. connect a USB/TTL 5V adapter to the TTL port 3. press the button and power on 4. use the memory dump batch file to dump the GME memory | 1. verify that the plain text FW is not present in the memory, indirectly this confirm that the flash encryption mechanism was triggered properly. | PASS | tested but in development mode, but is the same in release | A.Chiebao | 20200804
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## rtc configuration
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | RTC initialization with NTP reachable | 1. the device is powered off 2. a test AP configured 3. the default NTP server must be reachable, check it with a PC. 4. power on the device | Check with the debug console that the INT32 var that contain the UTC value, the number must be comparable with the current time returned by https://www.epochconverter.com/ | PASS |  | A.Chiebao | 20200804
2 | RTC initialization with NTP unreachable | 1. a test AP configured as previous test 2. set through the configuration page a bad NTP URI ie. "bad.ntp.org". 3. power on the device | Check with the debug console that the INT32 var that contain the UTC value, the converted value is within 1970/01/01 range use https://www.epochconverter.com/ GME must not reboot, it must be possible to reconfigure the ntp server using the web page | PASS |  | A.Chiebao | 20200804
3 | Test the power on time value | The system is running and correctly synchronized with the NTP server | Inspect the variable Power_On_Time in hello packet and this report the UTC time of start up | PASS | checked with epoch converter (www.epochconverter.com) | A.Chiebao | 20200804
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## wifi configuration
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | Test that device AP emit the right SSID | 1. A Windows PC with a WiFi adapter. Repeat all the below tests using a a smartphone. 2. device with AP mode in default condition | Use the PC/Smartphone to discover the SSID, you will find an SSID like "cgatem_ xxyyzz" where xxyyzz are tha last MAC address numbers of the device | PASS | tested with Androi smartphone and Windows PC | A.Chiebao | 20200804
2 | Test that device AP is connectable | 1. A Windows PC with a WiFi adapter (smartphone) 2. device with AP mode in default condition 3. Use the PC and connect to the SSID "cgatem_ xxyyzz" | 1. the PC is able to connect to the AP 2. the AP doesn't ask for a password 3. the DHCP of the device assign the address 10.10.100.10 to the PC 4. the default gateway returned is 10.10.100.254 Note. Use command line console with the "ipconfig /all" command to verify the above data. | PASS |  | A.Chiebao | 20200805
3 | Test that the device webserver respond | 1. A Windows PC with a WiFi connected to the AP | 1. open a browser and type "http://10.10.100.10" 2. the browser shows the device change credentials page | PASS | use the smartphone AP, the address is 192.168.43.254 | A.Chiebao | 20200806
4 | Test the device webserver change credentials page | 1. A Windows PC with a WiFi connected to the AP 2. test 3 completed | 1. the browser shows the device change cred page 2. insert new credentials and submit 3. the login page is shown (go to next test) | PASS |  | A.Chiebao | 20200807
5 | Test the device webserver login page | 1. A Windows PC with a WiFi connected to the AP | 1. the login page is able to receive the login information 2. When submit is clicked, the config page appears | PASS |  | A.Chiebao | 20200808
6 | Test the device webserver configuration page | 1. A Windows PC with a WiFi connected to the AP 2. browser pointing to "http://10.10.100.10". set the parameters as follow - AP SSID "your_ap" - AP Security : WPA - AP Password : "your_pwd" - DHCP on | 1. the page is properly shown 2. it is possible to see the list of reachable aps, selecting scan. 3. If dhcp is disabled static textboxes can be edited 4. show password boxes hide/show passwords 5. if ssid, password, ip in ap options are left blank the page is not submitted (password must be 8 characters) | PASS |  | A.Chiebao | 20200809
7 | Test that the device is able to connect to an AP manually selected | 1. a test AP connected to the internet configured as follow : - SSID "TEST_AP" - Security : WPA - Password : "12345678" - DHCP on 2. a device with all the connections parameter already configured as above | 1. the device is able to connect to the AP 2. through the debug console of the device, check that a. the IP address is 10.10.100.10 b. the default gateway is 10.10.100.254 c. the DNS is 8.8.8.8/8.8.4.4 | PASS |  | A.Chiebao | 20200810
8 | Test that the device is able to connect to an AP with hidden SSID | 1. a test AP connected to the internet configured as follow : - SSID "TEST_AP" with hidden SSID - Security : WPA - Password : "12345678" - DHCP on 2. a device with all the connections parameter already configured as above | 1. the device is able to connect to the AP 2. through the debug console of the device, check that a. the IP address is 10.10.100.10 b. the default gateway is 10.10.100.254 c. the DNS is 8.8.8.8/8.8.4.4 | PASS |  | A.Bilato | 20200915
9 | Test that the device is able to connect to an AP selected with a wifi scan | 1. a test AP connected to the internet configured as follow : - SSID "TEST_AP" - Security : WPA - Password : "12345678" - DHCP on 2. a device with all the connections parameter already configured as above 3. select the WPS choice and then press the WPS button on the AP (according to your AP manual) | 1. Check that hello message contains: a. part number (GTW000M2G0 for wifi model) b. hw version and fw version c. boot time (btm) which must be reasonable d. baud rate (which must coincide with that previously set) e. mqtt version, 3.1.1 f. Modbus addres of connected device (dev) g. model guid, retrieved from model file h. crc of model file i. cid, as described in tests above | PASS |  | A.Chiebao | 20200812
10 | Test that the device is able to connect to an AP configured with WPS | 1. check that every t_pst (configured with set_gw_config) a status message is sent | 1. Check that status message contains: a. epoch time of the moment message is sent b. upt, seconds since power on c. free memory (fme, in bytes) d. status of polling engine (est, 1 running, 2 stopped, 0 not valid) e. received signal strenght (sgn) (meaningful values around -60...-30 dBm | PASS | Not able to do that couse the AP(smartphone) can't hide the ssid retry in HQ with the D-Link modem, OK. | A.Chiebao | 20200813
11 | Test that gme keeps wps active for a limited period of time | 1. select WPS in web page and check current time | 1. Wait for more than 2 minutes before pressing button on wifi modem: connection is not possible (wps is no more active) | PASS | Not able to do that couse the AP(smartphone) can't hide the ssid retry in HQ with the D-Link modem, OK. | A.Chiebao | 20200814
12 | Test that the device is able to connect to an AP with static IP configuration | 1. a test AP connected to the internet configured as follow : - SSID "TEST_AP" - Security : WPA - Password : "12345678" 2. a device with all the connections parameter already configured as above 3. select DHCP off 4. fill the textboxes with IP address and other static configuration info | 1. the device is able to connect to the AP 2. through the debug console of the device, check that the IP address, the default gateway and the DNS are the ones configured | PASS | fixed a bug (resolved from version 84) | A.Chiebao | 20200815
13 | Test if the device configuration is maintained between power on/off cycle. | 1. if the previous tests are ok, power off the device and wait 5 seconds. 2. power on again the device | 1. the device is able to connect to the AP 2. through the debug console of the device, check that a. the IP address is 10.10.100.10 gateway is 10.10.100.254 c. the DNS is 8.8.8.8/8.8.4.4 3. open a browser and type "http://10.10.100.10" the device configuration page contains the values set in the previous test. | PASS |  | A.Chiebao | 20200816
14 | Test ntp server setting recovery | 1. in config page set a non existing ntp server, as bad.ntp.org) | 1. after reboot, check from debug console messages that time was not recovered 2. check that it is still possible to access the configuration page to reset the right server (pool.ntp.org) 3. verify that after a new reboot, time is properly obatined | PASS |  | A.Chiebao | 20200817
15 | Test change in ap options | 1. in config page, change ap ssid name and password | 1. after reboot, check that the GME is showing with new ap name and password | PASS |  | A.Chiebao | 20200818
16 | Test ap options hide ssid | 1. in config page, fill in mandatory textboxes then click Hide ssid | 1. after reboot, GME ssid is not visible with a scan from a PC or a phone, it can be manually set and connection must work | PASS |  | V.Cellini | 20200903
17 | Test if the configuration page accept only valid fields a. empty AP pwd not allowed b. |  | a. the system do not accept an empty pwd | PASS |  | A.Chiebao | 20200818
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## Wireless_Communication
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | Check that the system manage correctly the absence of Internet connection while the wireless connection is still present | GME configured and connected to the internet | - Timeout managed - the GME restore the connection as soon Internet is reacheable again | PASS | WiFi - simply use a router and detach the connection with the provider 2G - use a shielded dummy load on the antenna connector Pass after fix commit #763 | A.Chiebao | 20200804
2 | WiFi - Check that the GME connect only to an AP that have the right security level (WPA2) | - GME configured and connected to the internet - AP configured to accet only WEP | The GME refuse to connect | PASS |  | A.Chiebao | 20200805
3 | WiFi - Check that GME connect to an AP also if this is not initially available. | - GME configured and powered on - Test AP configured but powered off | The GME will connect to the AP within 2 min starting from the availability of the test AP | PASS | The scope of this test is to verify the robustness of the system after a global power fail, where every device have your own power up time. | A.Chiebao | 20200806
4 | WiFi - Check that GME reconnect to an AP initially available and after not reachable or powered off | - GME configured and connected to the internet - AP powered off / powered on again | The GME will reconnect to the AP within 2 min starting from the availability of the test AP | PASS |  | A.Bilato | 20200903
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## mqtt communication
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
0 |  | All below tests require that GME is connected to an AP and that a MQTT server is reachable. It also requires that a c.pCO is properly connected to the serial port of the GME, that configuration is completed and GME has a valid model on board. Use a proper application for c.pCO showing some alarm variables, and a reasonable number of HR, IR, DI and COIL. Use MQTTClientSimulatorBinary in http://svncarel.carel.com/svn/c780_carel_cloud_engine_binary/Utility/MqttClientSimulatorBinary/MqttClientSimulatorBinary This works as a sniffer and shows the decoded CBOR stream |  | PASS |  | A.Chiebao | 20200804
1 | payload-alarms.cbor | 1. the cpCO connected to the gateway 2. (A)select in the cpCO display the Alarm screen > select Coil_alr > change the value from 0 > 1 3. wait the first MQTT response 4. (B)select in the cpCO display the Alarm screen > select Coil_alr > change the value from 1 > 0 | Check that when the alarm is triggered a message is logged with st field containing the timestamp related to the beginning of the alarm, et 0. When the alarm reenters another alarm message is sent with st as the first message and et current time. Check all other fileds according to specification. | PASS |  | A.Chiebao | 20200805
2 | payload-set_lines_config.cbor | 1. the mqtt simulator sends a set_lines_config request to GME. | 1. GME gets new baud rate and new connector type and stores them in nvm 2. GME internally sets a flag in nvm to state that set_lines_config was done (it can be seen from debug console) 3. GME sends a response (only header) | PASS |  | A.Chiebao | 20200806
3 | payload-set_gw_config.cbor | 1. the mqtt simulator sends a set_gw_config request to GME. | 1. GME gets all data in request and saves it in nvm 2. GME internally sets a flag in nvm to state that set_gw_config was done (it can be seen from debug console) 3. GME sends a response (only header) | PASS |  | A.Chiebao | 20200807
4 | payload-set_devs_config.cbor | 1. the mqtt simulator sends a set_devs_config request to GME. | 1. GME reads all data in request 2. GME downloads the model from the url indicated in the model with provided credentials 3. GME internally sets a flag in nvm to state that set_devs_config was done (it can be seen from debug console) 4. GME sends a response (only header) 5. GME reboots 6. after reboot check that hello packet contains cid as in set_devs_config request, polling starts, values packets must contain did as in set_devs_config 7. after a further reboot, cid field in hello packet must be 0 | PASS |  | A.Chiebao | 20200808
5 | payload-set_devs_config.cbor with empty url | 1. the mqtt simulator sends a set_devs_config request to GME, with url field empty. | 1. GME clears internal flag to signal that device is not configured 2. GME sends a response 3. if set_lines and set_gw already received (which is the case), GME reboots 4. Polling does not start, hello contains cid field as in last request 5. after a further reboot, hello cointains cid field 0 | PASS |  | A.Chiebao | 20200809
6 | payload_connected.cbor | 1. as soon as GME starts and connects to mqtt server, it publishes connected payload | 1. Check that sent message contains: a. ts field, epoch time of connection to mqtt server (and check that this time is reasonable), b. sta field, 1 when GME connects to server, 0 as lwt (specificare meglio) | PASS | GTW000MWT0 for wifi model | A.Chiebao | 20200810
7 | payload-hello.cbor | 1. after connect message, an hello is sent | 1. Check that hello message contains: a. part number (GTW000M2G0 for wifi model) b. hw version and fw version c. boot time (btm) which must be reasonable d. baud rate (which must coincide with that previously set) e. mqtt version, 3.1.1 f. Modbus addres of connected device (dev) g. model guid, retrieved from model file h. crc of model file i. cid, as described in tests above | PASS | {"ver": 257 "t": 1596718264 "upt": 2110 "fme": 120752 "est": 2 "sgn": -22} est = stopped but the system are in polling mode, to check the C code. Different than the documentation. enum{ STOPPED = 0, INITIALIZED, RUNNING, NOT_INITIALIZED, }; | A.Chiebao | 20200811
8 | payload-status.cbor | 1. check that every t_pst (configured with set_gw_config) a status message is sent | 1. Check that status message contains: a. epoch time of the moment message is sent b. upt, seconds since power on c. free memory (fme, in bytes) d. status of polling engine (est, 1 running, 2 stopped, 0 not valid) e. received signal strenght (sgn) (meaningful values around -60...-30 dBm | PASS
9 | payload-scan_line.cbor | 1. the mqtt simulator sends a scan_line request to GME in different situations | 1. a c.pco with modbus address 1 is connected to GME 2. GME answers with a big message, which is the answer of the command 17 of c.pCO 3. a c.pCO with modbus address 5 is connected to GME 4. GME answers with a big message, which is the answer of the command 17 of c.pCO | PASS |  | A.Bilato | 20201005
10 | payload-change_credentials.cbor | 1. the mqtt simulator sends a change_credentials request to GME | 1. Verify that credentials are actually changed by looking at the debug console | PASS | all the team check implicity this conditions because is sent automatically by the IoT server | ALL
11 | payload-update_ca.cbor | 1. the mqtt simulator sends an update_ca request to GME | 1. GME attempts to download new cert from https server. It saves new cert to other memory location (not the one currently used). See debug console for confirm. 2. GME answers with a response (only header) | PASS |  | A.Chiebao | 20200811
12 | payload-update_dev_fw.cbor | 1. the mqtt simulator sends an update_dev_fw request to GME | 1. check with the oscilloscope that the serial communication is stopped 2. wait for response from GME saying if update was successful 3. whitin that period the cpCO will restart itself with the new application | PASS |  | A.Chiebao | 20200812
13 | payload-update_gw_fw.cbor | 1. the mqtt simulator sends an update_gw_fw request to GME | 1. check with the oscilloscope that the serial communication is stopped 2. wait for response from GME saying if update was successful 3. the gateway will restart itself with the new FW, the confirmation is when you receive the hello packet, verify the payload content: the "fwVersion" is updated to the new version | PASS | est value are equivalent to this enum enum{ STOPPED = 0, INITIALIZED, RUNNING, NOT_INITIALIZED, }; | A.Chiebao | 20200813
14 | payload-stop_engine.cbor | 1. Check that stop engine request actually stops polling | 1. Check that GME sends a response 2. Check that polling is stopped (no more values sent, even if some are forcedly changing) 3. Wait for a status message and check that est field is 2 | PASS | est value are equivalent to this enum enum{ STOPPED = 0, INITIALIZED, RUNNING, NOT_INITIALIZED, }; | A.Chiebao | 20200814
15 | payload-start_engine.cbor | 1. Check that start engine request actually starts polling | 1. Check that GME sends a response 2. Check that polling is started (values are sent, at sampling times if they are changing) 3. Wait for a status message and check that est field is 1 | PASS |  | A.Chiebao | 20200815
16 | payload-read_values.cbor | 1. Check that read_value message actually read Modbus values | 1. Attemp to read a value that is part of model 2. Check that GME answers with read value (compare it with that shown in pGD display) 3. Repeat test for each type of variable (coil, DI, IR, HR) 4. attempt to read a value that is not part of model 5. Verify steps 2 to 4 | PASS |  | A.Chiebao | 20200816
17 | payload-write_values.cbor | 1. Check that read_value message actually read Modbus values | 1. Attemp to write a value that is part of model 2. Check that GME answers as specified in RS 3. Repeat test for each type of variable (coil, DI, IR, HR) 4. attempt to read a value that is not part of model 5. Verify steps 2 to 4 | PASS |  | A.Chiebao | 20200817
18 | payload_values | 1. Check that values message is properly sent | 1. Check that values message is sent with high polling values at high sampling time 2. Check that values message is sent with low polling values at low sampling time 3. Check that no value message is sent if no change happened 4. Check that if no change happens during a T_pva (configured in set_gw_config), an empty message is sent) | PASS |  | A.Bilato | 20200922
19 | mqtt offline | 1. Cause an mqtt offline forcing down wifi network to which GME is connected |  | PASS |  | A.Bilato | 20200922
20 | payload-send_mb_adu-req |  |  |  | Not implemented in this step of project leave here for future reference | A.Bilato | 20200922
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## modbus communication
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | connettore RS485 | Set connector type RS485 with set_lines_config | Check that something is coming out from RS485 serial using an oscilloscope (for this to happen GME must have been previously configured, the same applies for successive tests) | PASS | i dont have an oscilloscope, i have try to write a digital riable (open/close a relay) | A.Chiebao | 20200804
2 | baud rate | a. Set baud rate to 9600 bps with a properly formed CBOR payload set_lines_config b. Set baud rate to 19200 bps with proper payload | In both cases, baud rate of the serial must change to the chosen values. Check with an oscilloscope or connecting a device having the required serial speed | PASS |  | V.Cellini | 20200826
3 | parity | a. Set parity to even b. Set parity to odd c. Set parity to none | Check with an oscilloscope | PASS |  | V.Cellini | 20200915
4 | stop bit | a. Set stop bit to 1 b. Set stop bit to 2 | Check with an oscilloscope | PASS | in the C code we don't manage the 1 or 2 stop bit due to the protocol only 2 | A.Bilato | 20200915
5 | connettore ttl | Set connector type ttl with set_lines_config | Check that something is coming out from ttl serial using an oscilloscope | PASS |  | A.Chiebao | 20200804
6 | repeat configuration tests for ttl connector (from #2 to #4) |  |  |  | not applicable we haven't the HW (IJ) | A.Bilato | 20200915
7 | polling delay 0 / 200 | a. Set polling delay to 0 b. Set polling delay to 200ms | Check with an oscilloscope. Verify that with polling delay 0 gme polls without delays between a packet and the following Verify that with polling delay 200 gme polls with 200ms delay between a packet and the following | PASS | with polling delay 0, interval between the end of the received packet and the transmission of the new packet is about 6.7ms with polling delay 200ms, delay between the end of the received packet and the transmission of the new packet is about 200ms. | V.Cellini | 20200915
8 | linearization | Use an application with 2 parameters having different linearization values. Change the 2 values | Verify that linearization is properly applied to both variables | PASS | float with A=2, B=1000, pCO value: 134,3 -> read value: 1268,6 float with A=5, =100, pCO value: 35,3 -> read value: 117,7 | V.Cellini | 20200826
9 | hysteresis | Use an application with 2 parameters having different hysteresis values. Change the 2 values |  | PASS | int32 having hysteresis 10 (start at 87, sent when 98); float having hyst 3.0 (start at 1.4, send when -1.7) | V.Cellini | 20200826
10 | Modbus offline |  |  | PASS | allarm device: {"ver": 257 "aty": 2 "ali": "" "aco": 1 "st": 1596721255 "et": 0 "did": 23} {"ver": 257 "aty": 2 "ali": "" "aco": 1 "st": 1596721255 "et": 1596721269 "did": 23} | A.Chiebao | 20200804
11 | model check (comprendendo anche il caso: "cosa succede se il modello è sbagliato per qualche ragione?") |  |  | PASS | the system generate offline o errors in corrispondence of the missing variables | A.Bilato | 20200922
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## CBOR encoding
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | Check robustness with respect to malformed headers | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor file whose header is badly formed | When GME receives the message, it detects the badly formed header, discards it and goes back to reception |  | Test done with IoT dept. During some session in July and August 2020 Tests from 1 to 14 aim at finding possible sw hunging when receiving badly formatted payloads. If a payload is syntactically correct but fields have data type different from expected, GME may have unpredictable behavior. | V.Cellini | xx/08/2020
2 | Check robustness with respect to malformed req_set_gw_config paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_set_gw_config file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2021
3 | Check robustness with respect to malformed req_set_line_config paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_set_line_config file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2022
4 | Check robustness with respect to malformed req_set_devs_config paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_set_devs_config file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2023
5 | Check robustness with respect to malformed req_scan_devices paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_scan_devices file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2024
6 | Check robustness with respect to malformed req_read_values paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_read_values file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2025
7 | Check robustness with respect to malformed req_write_values paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_write_values file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2026
8 | Check robustness with respect to malformed req_change_cred paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_change_cred file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2027
9 | Check robustness with respect to malformed req_gw_update paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_gw_update file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2028
10 | Check robustness with respect to malformed req_dev_update paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_dev_update file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2029
11 | Check robustness with respect to malformed req_reboot paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_reboot file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2030
12 | Check robustness with respect to malformed req_start_engine paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_start_engine file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2031
13 | Check robustness with respect to malformed req_stop_engine paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_stop_engine file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2032
14 | Check robustness with respect to malformed req_update_ca paylaod | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A cbor req_update_ca file whose payload is badly formed | When GME receives the message, it detects the badly formed payload, discards it and goes back to reception |  |  | V.Cellini | xx/08/2033
15 | Check connected payload | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a connected payload, it must contain all required fields, e.g. Connected: {“ver”:”100”, “ts”: 1574113297, “status”: 1} Check ts is correct time. |  |  | V.Cellini | xx/08/2034
16 | Check hello payload | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a hello payload, it must contain all required fields. Check fields content according to RS. |  |  | V.Cellini | xx/08/2035
17 | Check status payload (only wifi) | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a status payload, it must contain all required fields. Check fields content according to RS. Check it is sent every pst seconds. |  |  | V.Cellini | xx/08/2036
18 | Check mobile payload (only gsm) | 1. A Windows PC with MqttClientSimulatorBinary installed | When GME sends a mobile payload, it must contain all required fields. Check fields content according to RS. Check it is sent every 5 minutes. |  |  | V.Cellini | xx/08/2037
19 | Check alarms payload | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A c.pCO family controller connected | Force an alarm, check alarm payload is received and check fields content according to RS. Remove the alarm, check again alarm payload is received with proper fields in it. |  |  | V.Cellini | xx/08/2038
20 | Check values payload | 1. A Windows PC with MqttClientSimulatorBinary installed 2. A c.pCO family controller connected | Check values payload is received and check fields content according to RS. |  | This test does not aim at tyesting everything about values payload but just that syntax is correct. | V.Cellini | xx/08/2039
21
22
23
24
25
26
27
28
29
30
31
32
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## default config
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | Check default configuration is triggered by pressing button with specific procedure | 1. GME regularly running |  | PASS |  | A.Bilato | 2020-10-01
2 | Check that after default configuration is triggered, GME actually starts with default configuration | 1. GME regularly running |  | PASS |  | A.Bilato | 2020-10-01
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## gsm configuration
Test ID | Summary | Preconditions | Expected Result | Result | Notes | Who | When
1 | Verify if the official CAREL SIM connect to our server | 1. the IMEI of the device under test is registered on CAREL cloud 2. power on the system | Through the RED portal or through the test program in a short time < 5 min you will see the Hello message from the GME | PASS |  | A.Bilato | 2020-10-01
Note on B1: Brief description of the scope of the test
Note on C1: Test preconditions ie. Status of the connection, status of the monitored device etc.
Note on D1: Expected Result
Note on F1: if something was wrong a brief explanation of what happened

## Support
Test result
PASS
FAIL
BLOCKING